## Slide 1
One-Way Delay over C37.94 with Zeus
Guide & Slides corresponding to software ver. 2.3.11
C37.94 Testing

## Slide 2: Zeus & xGenius
Zeus & xGenius provide deep insights to design, install, maintain, troubleshoot and engineer communications resources of Mobile Operators, Power Utilities, Finace, Labs and R+D centers. The unit is able to verify Ethernet/IP, SyncE, PTP, GbE, IRIG-B, 1PPS, T1/E1, G703, Serial Datacom, C37.94, GOOSE, SV, MMS, Round-trip & One-way Delay tests at all interfaces.
It also has a set of programmable filters to capture live data traffic at wire-speed

## Slide 3: Interfaces & time References
The unit is equipped with GNSS receiver with SMA female connector for connecting an antenna typically supplied with a 5 m of coaxial cable plus a 10 m extension cable.
 | GNSS | PTP | NTP | ToD | IRIG-B | PPS | PP2S | SyncE | T1/E1 | MHz | C.3794
RJ45-A |  | in/out | in/out |  |  |  |  | in/out |  |  | 
RJ45-B |  |  |  |  |  |  |  | in/out |  |  | 
SFP-A |  | in/out | in/out |  |  |  |  | in/out |  |  | 
SFP-B |  |  |  |  |  |  |  | in/out |  |  | 
BNC-C |  |  |  |  |  |  |  |  | in/out | in/out | 
RJ45-C |  |  |  | in |  | in | in |  | in/out | in/out | 
SMB-C |  |  |  |  |  |  |  |  |  |  | 
SMA | in |  |  |  |  |  |  |  |  |  | 
SMB-1 |  |  |  |  | in | in | in |  |  |  | 
SMB-2 |  |  |  |  | out | out | out |  |  |  | 
RJ-45 |  |  |  | in/out | in/out | in/out | in/out |  | in/out | in/out | 
PHM |  |  |  |  |  |  |  |  |  |  | in/out
PHM
RJ45-C
BNC-C
RJ45-A
RJ45-B
SFP-B
SFP-A
Micro SD
SMB-2
SMB-1
SMA
SMB-C
RJ45

## Slide 4: One-Way Delay over C37.94 Interface
IEEE C37.94
VT
CT
CB
IED
Low Voltage
SDH/SONET
VT
CT
CB
S U B S T A T I O N - 1
S U B S T A T I O N - 2
IEEE C37.94
ALBEDO
xGenius
ALBEDO
xGenius
High Voltage
GNSS
GNSS
Protection schemes, such as C37.94, have the objective of keeping the Power System stable and isolated. For correct function the control of latency, latency variations and asymmetry is fundamental.
Zeus and xGenius equipped with C37.94 interfaces and synchronized by GPS, measure all key parameters including One‐Way Delay (OWD) by means of two units (in the picture A and B) at the ends of the path to be qualified.
Testing Points
A
B

## Slide 5: Connecting the GPS & C37.94
Zeus / xGenius are equipped with C47.94 optical interfaces and a built-in GNSS receiver. Proceed to connect all the elements:
Introduce a couple of compatible SFP to the C37.94 ports
Connect the optical cables to the SFPs into Port A (Port B is not enabled)
Connect the cable to the SMA and orient the antenna oriented to open sky
Repeat the same operation in Tester B
3
1
2

## Slide 6: Steps to connect the built-in GNSS
Home > Config > Reference clock > Input clock := GNSS (*)
Press LEDS to check the status
Wait for the REF and LOCK LEDs to become green
(*) Go to Home panel, go to Config, the port setup will be displayed then Go to Reference clock and configure Input clock to GNSS.
1
2
1
3

## Slide 7: OCXO or Rubidium
  The unit will be ready for testing LOCK LED is green
  Mind that time is different depending which oscillator xGenius is equipped
Current locking status (Locking, Fine locking, Locked, Holdover, etc.) can be checked in the Reference clock menu.
Metric | OCXO | Rubidium
Locking time | < 5 minutes | < 4 hours
1

## Slide 8: Configuring the GNSS Properties
Configure the GNSS to increase the accuracy:
Config > Reference clock > GNSS receiver > Antenna cable delay to configure a compensation at the correction field
In the same screen Enable/Disable any constellation (GPS, GLONASS, GALILEO, BEIDO) through the Active GNSS setting := GPS…
Go to Fixed‐position mode := Auto-average
1
2
3

## Slide 9: Position Averaging time
GPS has a statistical distribution and averaging for a time filters errors to improve accuracy.
Adjust the Position averaging time and by configuring Auto‐average in the that now displays Averaging
Wait to the Fixed position status to become Active. The unit is now ready for testing.
Note: Theoretically, testing could start before the end of the position averaging process. The improved time estimation due to this function would be automatically applied starting from the end of the auto‐averaging process.
Notes: (a) At least 1h of averaging is required for reasonable accuracy. (b) The procedure should be run only once as long as the location does not change. If any change is detected (longitude, latitude, altitude) an error will be displayed.
1
2

## Slide 10: Holdover mode
When GPS is not available (i.e. a room without windows) you can first synchronize the unit in a place with GPS and then go to execute the test in holdover mode.
Accuracy will depend on: (a) the quality of the internal oscillator (Quartz, OCXO, Rubidium); and (b) the holdover period.
Synchronize to GPS and and verify that LED Clock, REF and LOCK are green
Config > Reference clock > Holdover duration := set the time you need for testing
Config > Reference clock > Force holdover := Yes
1
2
3

## Slide 11: Hands-on to C37.94 test
We are going to explain the One-way delay using two testers, however Zeus / xGenius can execute also a number of tests including:
  Measuring Frequency, Bit Rate and Optical Power
  Running BER and Performance Tests
  Event Generation and Analysis
  Latency measurement
  Jitter and Wander Generation and Analysis
Teleprotection
Multiplexer
GNSS
Generation Analysis
Loopback
A
B

## Slide 12: Enable the C37.94 analysis
Go to Home > Config > Mode > C37.94 Endpoint
Enable optical transmission Port A > Enable := yes
Configure tester A to Generate & Analyze traffic: Config > Port Mode := TX/RX
Repeat the configuration in Tester B
Attention: Remember to use Port A for delay tests, no Port B
3
2
4
1

## Slide 13: Configure clocks
In tester A: Configure TX clock source, TX clock offset (ppm), Frame, TX data rate / TX timeslots and Test pattern to match your network settings
In tester B: Configure TX clock source, TX clock offset (ppm), Frame, TX data rate / TX timeslots and Test pattern to match your network settings
Set laser Config > Port A > Laser := On
Pattern LSS should be in green indicating continuity between testers A and B
1/2
1/2
1/2
4
3

## Slide 14: Enable the OWD test
Go to tester A: Test > Delay test > Enable := Yes
Configure to One‐way: Test > Measurement mode := One way
Repeat the configuration in tester B.

## Slide 15: Adjust to Zero
It is necessary to cancel the delay due to cables and intrinsic to the tester that could modify the results.
Disconnect the unit from the network and loop Tx - Rx with a patch cord
Test > Delay test > Adjust zero offset := Auto-calibrate
Go to Results > Delay (All delay parameters shall be zero)
Once you have calibrated the OWD test, reconnect the unit to the network.
Repeat the configuration in tester B
3
2
1

## Slide 16: Running the OWD test
The test is now ready to start then Press RUN Check Delay results at any time during the testing process:
Home > Results > Delay test
2

## Slide 17: Event logger enable
Global counts, statistics and LEDs provide information about which events and how many of them have been registered but they do not say too much about how they are distributed in time. These information is supplied at the Event Logger a graphical representation tool that permits to trace the evolution of key parameters.
The first thing to to is to enable it:
Go to Home > Test > Event logger setup
Set Enable := Yes
1
1

## Slide 18: Configuring the Event Logger
Traceable Events are categorized in different classes. Moreover, each test port has its own traceable events. These events may be different for each test port.
Clear the currently selected filters: Clear all filters := Yes
Select the events: Port A > Delay := Round trip | Forward | Return | Asymmetry
Choose the events to trace: Anomalies/defects | Bandwidth statistics | Frame layer statistics | SLA statistics | BERT | PTP | NTP | Synchronization
Press Run to begin the generation of a trace file
1
3
2
4

## Slide 19: Display the logs
With the Event Logger you can select one or various events and trace them so that all changes along with the time and date these changes are registered are recorded with a 1 second resolution. The event logger provides representations and zoom levels to enable event analysis at different time scales:
Go to Results > Event logger
Analyze all the delay parameters displayed
1
2

## Slide 20: Event logger results
You can display the trace of the evolution of the previously selected parameters:
View and analyze the details of the histogram
Set the scale at your preferred zoom level
Selected OWD.RET (one way delay) event to display a more detailed diagram
Click on the screen to know the exact value at one specific time
4
4
6
2
2
2
1
3

## Slide 21: Scaling the trace
To change the scale horizontally click one time, for vertical two times
Click in the red buttom and draw to the left or to the right
To change the scale vertically click two times
To move the trace across the time click one of the three the red buttoms and draw the finger up and down
Click in the auto-scale symbol to return to the initial conditions
1
1
2
1
5

## Slide 22: Exporting Logs
To export log files in CSV format:
Go Home > [File icon] > Configuration files | Report files > Internal memory to list the files currently stored in the unit
Select the files you want to export: File name > Export
Choose an external device: micro SD | USB
If no external device a popup will appear: ‘No devices present’
2
3
1
1

## Slide 23: Glossary
AAA: Authentication, Authorization, and Accounting
ACL: Access Control List
AP: Access Point
Busbar: Metallic strip or bar, typically housed inside switchgear, panel boards, and busway enclosures for local high current power distribution C37.94: TDM interface devoted for teleprotection
CB: Circuit Breaker designed to close or open electrical circuit under normal or abnormal conditions. It operates on relays command.
CBWFQ: Class-Based Weighted Fair Queuing
CG: Connected Grid
CID: Individual configuration of each IED CIP: Critical Infrastructure Protection CLI: Command-Line Interface
CorpSS: Corporate Substation
CT: Current Transformer, used for measurement of current, if too high to apply directly to measuring instruments, a CT produces a proportional current which can be measured and recorded, CT are used in metering and protective relays
DAN: Doubly Attached Nodes implementing HSR or PRP
DAU: Data Acquisition Unit
Disconnector: isolates physically and visually the lines
DMZ: Demilitarized Zone
DCB: Directional Comparison Blocking
DCS: distributed control systems
DSC: Differentiated Services Code Point
ESP: Electronic Security Perimeter
Feeder: Transmits power to the distribution points
GM: Grandmaster
GNSS: Global Navigation Satellite System
GOOSE: Generic Object-Oriented Substation Events is a control model defined as per IEC 61850 which provides a fast and reliable mechanism of transferring event data over entire electrical substation networks. When implemented, this model ensures the same event message is received by multiple physical devices using multicast or broadcast services
HMI: Human Machine Interface
PTP: Precision Time Protocol
RedBox: Redundancy Box
Relay: is automatic device which senses an abnormal condition of electrical circuit and closes its contacts and complete the circuit breaker trip.
REP: Resilient Ethernet Protocol
RCT: Redundancy Control Trailer
RTU: Remote Terminal Unit
SA: Substation Automation
SAN: Singly-Attached Node
Secondary Lines: lower voltage side at the substation
SCADA: Supervisory Control And Data Acquisition, transmits and receives data from events of controls, measuring, safety and monitoring. Power system elements can be controlled remotely over. Remote switching, telemetering of grids showing voltage, current, power, direction, consumption in kWh, synchronization.
SCD: Substation Configuration Description SCL: Substation Configuration Language SNTP: Simple Network Time Protocol
Station Bus: Connects the entire substation and helps provide connectivity between central management and individual bays
STP: Spanning Tree Protocol
SV: Sampled Values, is a method to read instantaneous values such as currents, voltages, impedances, etc. from CTs, VTs or digital I/O and then transmitted to make them are available for those IED subscribed.
Switchgear: combination of switches, fuses or CB to control, protect and isolate electrical equipment
SyncE: Synchronous Ethernet
TLV: Type, Length, Value
VT: Voltage Transformer (see CT)Potential Transformer, gives the reference voltage to the Relay for Over-voltage or Under-voltage Protection
UCA IuG: Utility Communications Architecture International Users Group
VDAN: Virtual D
HQoS: Hierarchical Quality of Service
HSR: High-Availability Seamless Redundancy
IA: Industrial Automation
ICS: Industrial control systems
ICU: Intelligent Control Unit
IEC: International Electrotechnical Commission
IEC 61850: Standard defining communication protocols for intelligent electronic devices at electrical substations
IED: Intelligent End Device, microprocessor-based controllers of power system equipment, such as circuit breakers, transformers and capacitor banks to enable advanced power automation.
IRIG: Inter-Range Instrumentation Group
ISE: Identity Services Engine
L3VPN: Layer 3 Virtual Private Network
LA: Lightning Arrester protects the power grid from electric storms
MQC: Modular QoS Command-Line Interface
MMS: Manufacturing Message Specification, messaging system for exchanging real-time data and supervisory control information. Allows client such as SCADA, an OPC server or a gateway to access all IED objects MPLS: Multi-protocol Label Switching
MU: Merging Unit connected to the process bus converts analog data(ie. volts, currect...) into digital information
NERC: North American Electric Reliability Corporation
NIST: National Institute of Standards and Technology
NMS: Network Management System
OAM: Operations and Maintenance
PCP: Priority Code Point
PIOC: Instantaneous overcorrent Protection
PLC: Programmable Logic Controller
PMU: Phasor Measurement Unit
POTT: Permissive Overreaching Transfer Trip
PP: Primary Power
Process Bus: Connects primary units and control equipment to the IEDs
PRP: Parallel Redundancy Protocol
PRTC: Primary Reference Clock
PT: see VT
T-GM: Grand Master PTP
T-BC: Boundary Clock
T-TSC: Slave Clock

## Slide 24
That’s all
www.albedotelecom.com